## Sheet1
Function Code 03 - Read holding Registers.
Register | Query Address | Size | Measurement | Notes
UPS Information Group
40001 - 40007 | 0000 - 0006 | 14 characters | UPS Company Name | 14 characters
40008 - 40012 | 0007 - 0011 | 10 characters | UPS Model | 10 characters
40013 - 40017 | 0012 - 0016 | 10 characters | version number of the UPS firmware | 10 characters
40018 - 40025 | 0017 - 0024 | 16 characters | firmware revision of the UPS SNMP Proxy agent. | 16 characters
Battery Group
40026 | 0025 | UWORD | Battery Status | Integer Value: unknown(1),batteryNormal(2),batteryLow(3)
40027 | 0026 | UWORD | Seconds on Battery | Seconds
40028 | 0027 | UWORD | Battery Capacity | 0-100%
40029 | 0028 | UWORD | Battery Voltage | x0.01 VAC
40030 | 0029 | UWORD | Battery Temperature | x0.1 ℃
40031 | 0030 | UWORD | Battery Current | x0.1 A
Input Group
40040 | 0039 | UWORD | Input Line Voltage | x0.1 VAC
40041 | 0040 | UWORD | Input Max Line Voltage | x0.1 VAC
40042 | 0041 | UWORD | Input Min Line Voltage | x0.1 VAC
40043 | 0042 | UWORD | Input Frequency | x0.1 Hz
Output Group
40050 | 0049 | UWORD | Output Status | Integer Value:unknown(1),onLine(2),onBattery(3),onBoost(4),sleeping(5),onBypass(6),rebooting(7),standBy(8),onBuck(9)
40051 | 0050 | UWORD | Output Voltage | x0.1 VAC
40052 | 0051 | UWORD | Output Frequency | x0.1 Hz
40053 | 0052 | UWORD | Output Load | 0-100%
|  | UWORD | Rating Group
40060 | 0059 | UWORD | Rating Voltage | x0.1 VAC
40061 | 0060 | UWORD | Rating Power | VA
40062 | 0061 | UWORD | Rating Battery Voltage | x0.01 VAC
40063 | 0062 | UWORD | Rating Frequency | x0.1 Hz
Function Code 06 - Write Single Register
Function Code 16 - Write Multiple Registers
Config Group
40070 | 0069 | UWORD | Config ups Shut off Delay | The delay in seconds the UPS remains on after being told to turn off. Allowed values are 12, 18, 24, 30, 36, 42, 48, 54, 60, 120, 180, 240, 300, 360, 420, 480, 540, and 600 seconds.
40071 | 070 | UWORD | Config Ups Sleep Time | Integer Value: 1 - 9999
Control Group
40080 | 0079 | UWORD | Control UPS Off | Integer Value: turnUpsOff(2)
40081 | 0080 | UWORD | Control Reboot Ups | Integer Value: rebootUps(2)
40082 | 0081 | UWORD | Control UPS Sleep | Integer Value: noPutUpsToSleep(1),putUpsToSleep(2)
40083 | 0082 | UWORD | Control Simulate Power Fail | Integer Value: simulatePowerFailure(2)
40084 | 0083 | UWORD | Control Flash And Beep | Integer Value: flashAndBeep(2)
40085 | 0084 | UWORD | Control Turn On UPS Load | Integer Value: upsSmartControlTurnOnUpsLoad(2)
Test Group
40090 | 0089 | UWORD | Test Diagnostics | Integer Value: testDiagnostics(2)
Function Code 03 - Read holding Registers.
40091 | 0090 | UWORD | Test Diagnostics Results | Integer Value: ok(1),failed(2),invalidTest(3),testInProgress(4)
ThreePhase UPS
Battery Group
40100 | 0099 | UWORD | Battery Voltage | VAC
40101 | 0100 | UWORD | Battery Capacity | 0-100%
40102 | 0101 | UWORD | Battery Time Remain | Minutes
40103 | 0102 | UWORD | Battery Current | x0.1 A
40104 |  |  | Battery Temperature | x0.1 ℃
Input Group
40110 | 0109 | UWORD | Input Frequency | x0.1 Hz
40111 | 0110 | UWORD | Input Voltage R | x0.1 VAC
40112 | 0111 | UWORD | Inpu tVoltage S | x0.1 VAC
40113 | 0112 | UWORD | Input Voltage T | x0.1 VAC
Output Group
40120 | 0119 | UWORD | Output Frequency | x0.1 Hz
40121 | 0120 | UWORD | Output Voltage R | x0.1 VAC (Output Voltage in the threeInOneOut)
40122 | 0121 | UWORD | Output Voltage S | x0.1 VAC (equivalent to Register 40124 in the threeInOneOut)
40123 | 0122 | UWORD | Output Voltage T | x0.1 VAC (equivalent to Register 40101 in the threeInOneOut)
40124 | 0123 | UWORD | Output Load Percentage R | x0.1 Percentage(Output Load Percentage in the threeInOneOut)
40125 | 0124 | UWORD | Output Load Percentage S | x0.1 Percentage (No significance in the threeInOneOut)
40126 | 0125 | UWORD | Output Load Percentage T | x0.1 Percentage (No significance in the threeInOneOut)
Bypass Group
40130 | 0129 | UWORD | Bypass Source Frequency | x0.1 Hz
40131 | 0130 | UWORD | Bypss Source Voltage R | x0.1 VAC
40132 | 0131 | UWORD | Bypss Source Voltage S | x0.1 VAC
40133 | 0132 | UWORD | Bypss Source Voltage T | x0.1 VAC
UPS Status Group
40140 | 0139 | UWORD | DC and Rectifier Status RecRotError | Integer Value: yes(14),no(16)
40141 | 0140 | UWORD | DC and Rectifier Status LowBatteryShutdown | Integer Value: yes(14),no(16)
40142 | 0141 | UWORD | DC and Rectifier Status LowBattery | Integer Value: yes(14),no(16)
40143 | 0142 | UWORD | DC and Rectifier Status InAndOut | Integer Value: threeInOneOut(2),threeInThreeOut(3)
40144 | 0143 | UWORD | DC and Rectifier Status BatteryStatus | Integer Value: backup(4),acnormal(5)
40145 | 0144 | UWORD | DC and Rectifier Status ChargeStatus | Integer Value: boost(6),float(7),no(16)
40146 | 0145 | UWORD | DC and Rectifier Status RecOperating | Integer Value: yes(14),no(16)
40147 | 0146 | UWORD | UPS Status Bypass Freqency Fail | Integer Value: yes(14),no(16)
40148 | 0147 | UWORD | UPS Status Manual Bypass Breaker | Integer Value: close(8),open(9)
40149 | 0148 | UWORD | UPS Status AC Status | Integer Value: normal(10),abnormal(11)
40150 | 0149 | UWORD | UPS Status Static Switch Mode | Integer Value: invermode(12),bypassmode(13)
40151 | 0150 | UWORD | UPS Status Inverter Operating | Integer Value: yes(14),no(16)
Fault Status Group
40160 | 0159 | UWORD | Fault Status Emergency Stop | Integer Value: yes(14),no(16)
40161 | 0160 | UWORD | Fault Status High DC Shutdown | Integer Value: yes(14),no(16)
40162 | 0161 | UWORD | Fault Status Bypass Breaker | Integer Value: yes(14),no(16)
40163 | 0162 | UWORD | Fault Status Over Load | Integer Value: yes(14),no(16)
40164 | 0163 | UWORD | Fault Status Inverter Output Fail | Integer Value: yes(14),no(16)
40165 | 0164 | UWORD | Fault Status Over Temperature | Integer Value: yes(14),no(16)
40166 | 0165 | UWORD | Fault Status Short Circuit | Integer Value: yes(14),no(16)
Rating Group
40170 - 40176 | 0169 - 0175 | 14 characters | Rating Rectifier Voltage | 14 characters
40177 | 0176 | UWORD | Rating Rectifier Frequency | Hz
40178 - 40184 | 0177 - 0183 | 14 characters | Rating Source Bypass Voltage | 14 characters
40185 | 0184 | UWORD | Rating Bypass Source Frequency | Hz
40186 - 40192 | 0185 - 0191 | 14 characters | Rating Output Voltage | 14 characters
40193 | 0192 | UWORD | Rating Output Frequency | Hz
40194 | 0193 | UWORD | Rating Battery Voltage | VAC
40195 - 40199 | 0194 - 0198 | 10 characters | Rating Power | 10 characters
UPS Environment
Function Code 03 - Read holding Registers.
Environment Status
40301 | 0300 | UWORD | Environment Temperature | x0.1 ℃
40302 | 0301 | UWORD | Environment Humidity | 0-100%
40303 | 0302 | UWORD | Environment Water | Integer Value: normal(1),abnormal(2)
40304 | 0303 | UWORD | Environment Smoke | Integer Value: normal(1),abnormal(2)
40305 | 0304 | UWORD | Environment Security1 | Integer Value: normal(1),abnormal(2)
40306 | 0305 | UWORD | Environment Security2 | Integer Value: normal(1),abnormal(2)
40307 | 0306 | UWORD | Environment Security3 | Integer Value: normal(1),abnormal(2)
40308 | 0307 | UWORD | Environment Security4 | Integer Value: normal(1),abnormal(2)
40309 | 0308 | UWORD | Environment Security5 | Integer Value: normal(1),abnormal(2)
40310 | 0309 | UWORD | Environment Security6 | Integer Value: normal(1),abnormal(2)
40311 | 0310 | UWORD | Environment Security7 | Integer Value: normal(1),abnormal(2)
Environment Settings
40312 | 0311 | UWORD | Environment Over Temperature | x0.1 ℃
40313 | 0312 | UWORD | Environment Under Temperature | x0.1 ℃
40314 | 0313 | UWORD | Environment Over Humidity | 0-100%
40315 | 0314 | UWORD | Environment Under Humidity | 0-100%
Function Code 06 - Write Single Register
Function Code 16 - Write Multiple Registers
Environment Settings
40401 | 0400 | UWORD | Environment Over Temperature | x0.1 ℃
40402 | 0401 | UWORD | Environment Under Temperature | x0.1 ℃
40403 | 0402 | UWORD | Environment Over Humidity | 0-100%
40404 | 0403 | UWORD | Environment Under Humidity | 0-100%